## Hoja1
Reg# | Size | Description | Format
1000 | 2 | V A-N | FLOAT
1002 | 2 | V B-N | FLOAT
1004 | 2 | V C-N | FLOAT
1006 | 2 | V A-B | FLOAT
1008 | 2 | V B-C | FLOAT
1010 | 2 | V C-A | FLOAT
1012 | 2 | I A | FLOAT
1014 | 2 | I B | FLOAT
1016 | 2 | I C | FLOAT
1018 | 2 | W, Total | FLOAT
1020 | 2 | VAR, Total | FLOAT
1022 | 2 | VA, Total | FLOAT
1024 | 2 | PF, Total | FLOAT
1026 | 2 | Frequency | FLOAT
1028 | 2 | I Neutral | FLOAT
1030 | 2 | W, Phase A | FLOAT
1032 | 2 | W, Phase B | FLOAT
1034 | 2 | W, Phase C | FLOAT
1036 | 2 | VAR, Phase A | FLOAT
1038 | 2 | VAR, Phase B | FLOAT
1040 | 2 | VAR, Phase C | FLOAT
1042 | 2 | VA, Phase A | FLOAT
1044 | 2 | VA, Phase B | FLOAT
1046 | 2 | VA, Phase C | FLOAT
1048 | 2 | PF, Phase A | FLOAT
1050 | 2 | PF, Phase B | FLOAT
1052 | 2 | PF, Phase C | FLOAT
1054 | 2 | Symmetrical Component Magnitude, 0 sequence component | FLOAT
1056 | 2 | Symmetrical Component Magnitude, positive sequence | FLOAT
1058 | 2 | Symmetrical Component Magnitude, negative sequence component | FLOAT
1060 | 1 | Symmetrical Component Phase, zero sequence component | SINT16
1061 | 1 | Symmetrical Component Phase, positive sequence component | SINT16
1062 | 1 | Symmetrical Component Phase, negative sequence component | SINT16
1063 | 1 | Voltage Unbalance, zero sequence component component | UINT16
1064 | 1 | Voltage Unbalance, negative sequence component | UINT16
1065 | 1 | Current Unbalance | UINT16
1066 | 1 | Quadrant indicator | UINT16
1067 | 2 | Q Total | FLOAT
1069 | 2 | Q Phase A | FLOAT
1071 | 2 | Q Phase B | FLOAT
1073 | 2 | Q Phase C | FLOAT
1500 | 2 | Wh, (Q1+Q4) | SINT32
1502 | 2 | Wh, (Q2+Q3) | SINT32
1504 | 2 | Wh, Net | SINT32
1506 | 2 | Wh, Total | SINT32
1508 | 2 | VARh, (Q1+Q2) | SINT32
1510 | 2 | VARh, (Q3+Q4) | SINT32
1512 | 2 | VARh, Net | SINT32
1514 | 2 | VARh, Total | SINT32
1516 | 2 | VAh, Total | SINT32
1518 | 2 | Wh, (Q1+Q4), Phase A | SINT32
1520 | 2 | Wh, (Q1+Q4), Phase B | SINT32
1522 | 2 | Wh, (Q1+Q4), Phase C | SINT32
1524 | 2 | Wh, (Q2+Q3), Phase A | SINT32
1526 | 2 | Wh, (Q2+Q3), Phase B | SINT32
1528 | 2 | Wh, (Q2+Q3), Phase C | SINT32
1530 | 2 | Wh, Net, Phase A | SINT32
1532 | 2 | Wh, Net, Phase B | SINT32
1534 | 2 | Wh, Net, Phase C | SINT32
1536 | 2 | Wh, Total, Phase A | SINT32
1538 | 2 | Wh, Total, Phase B | SINT32
1540 | 2 | Wh, Total, Phase C | SINT32
1542 | 2 | VARh, (Q1+Q2), Phase A | SINT32
1544 | 2 | VARh, (Q1+Q2), Phase B | SINT32
1546 | 2 | VARh, (Q1+Q2), Phase C | SINT32
1548 | 2 | VARh, (Q3+Q4), Phase A | SINT32
1550 | 2 | VARh, (Q3+Q4), Phase B | SINT32
1552 | 2 | VARh, (Q3+Q4), Phase C | SINT32
1554 | 2 | VARh, Net, Phase A | SINT32
1556 | 2 | VARh, Net, Phase B | SINT32
1558 | 2 | VARh, Net, Phase C | SINT32
1560 | 2 | VARh, Total, Phase A | SINT32
1562 | 2 | VARh, Total, Phase B | SINT32
1564 | 2 | VARh, Total, Phase C | SINT32
1566 | 2 | VAh, Phase A | SINT32
1568 | 2 | VAh, Phase B | SINT32
1570 | 2 | VAh, Phase C | SINT32
1572 | 2 | Wh, (Q1), Total | SINT32
1574 | 2 | VARh, (Q1), Total | SINT32
1576 | 2 | VAh, (Q1),Total | SINT32
1578 | 2 | Wh, (Q1), Phase A | SINT32
1580 | 2 | Wh, (Q1), Phase B | SINT32
1582 | 2 | Wh, (Q1), Phase C | SINT32
1584 | 2 | VARh, (Q1), Phase A | SINT32
1586 | 2 | VARh, (Q1), Phase B | SINT32
1588 | 2 | VARh, (Q1), Phase C | SINT32
1590 | 2 | VAh, (Q1), Phase A | SINT32
1592 | 2 | VAh, Phase B | SINT32
1594 | 2 | VAh, (Q1), Phase C | SINT32
1596 | 2 | Wh, (Q2), Total | SINT32
1598 | 2 | VARh, (Q2), Total | SINT32
1600 | 2 | VAh, (Q2), Total | SINT32
1602 | 2 | Wh, (Q2), Phase A | SINT32
1604 | 2 | Wh, (Q2), Phase B | SINT32
1606 | 2 | Wh, (Q2), Phase C | SINT32
1608 | 2 | VARh, (Q2), Phase A | SINT32
1610 | 2 | VARh, (Q2), Phase B | SINT32
1612 | 2 | VARh, (Q2), Phase C | SINT32
1614 | 2 | VAh, (Q2), Phase A | SINT32
1616 | 2 | VAh, (Q2), Phase B | SINT32
1618 | 2 | VAh, (Q2), Phase C | SINT32
1620 | 2 | Wh, (Q3), Total | SINT32
1622 | 2 | VARh, (Q3), Total | SINT32
1624 | 2 | VAh, (Q3), Total | SINT32
1626 | 2 | Wh, (Q3), Phase A | SINT32
1628 | 2 | Wh, (Q3), Phase B | SINT32
1630 | 2 | Wh, (Q3), Phase C | SINT32
1632 | 2 | VARh, (Q3), Phase A | SINT32
1634 | 2 | VARh, (Q3), Phase B | SINT32
1636 | 2 | VARh, (Q3), Phase C | SINT32
1638 | 2 | VAh, (Q3), Phase A | SINT32
1640 | 2 | VAh, (Q3), Phase B | SINT32
1642 | 2 | VAh, (Q3), Phase C | SINT32
1644 | 2 | Wh, (Q4), Total | SINT32
1646 | 2 | VARh, (Q4), Total | SINT32
1648 | 2 | VAh, (Q4), Total | SINT32
1650 | 2 | Wh, (Q4), Phase A | SINT32
1652 | 2 | Wh, (Q4), Phase B | SINT32
1654 | 2 | Wh, (Q4), Phase C | SINT32
1656 | 2 | VARh, (Q4), Phase A | SINT32
1658 | 2 | VARh, (Q4), Phase B | SINT32
1660 | 2 | VARh, (Q4), Phase C | SINT32
1662 | 2 | VAh, (Q4), Phase A | SINT32
1664 | 2 | VAh, (Q4), Phase B | SINT32
1666 | 2 | VAh, (Q4), Phase C | SINT32
1668 | 2 | VAh, (Q1+Q4), Total | SINT32
1670 | 2 | VAh, (Q1+Q4), Phase A | SINT32
1672 | 2 | VAh, (Q1+Q4), Phase B | SINT32
1674 | 2 | VAh, (Q1+Q4), Phase C | SINT32
1676 | 2 | VAh, (Q2+Q3), Total | SINT32
1678 | 2 | VAh, (Q2+Q3), Phase A | SINT32
1680 | 2 | VAh, (Q2+Q3), Phase B | SINT32
1682 | 2 | VAh, (Q2+Q3), Phase C | SINT32
1684 | 2 | It, Phase A | UINT32
1686 | 2 | It, Phase B | UINT32
1688 | 2 | It, Phase C | UINT32
1690 | 2 | It, Phase N | UINT32
1692 | 2 | Vt, Phase A-N | UINT32
1694 | 2 | Vt, Phase B-N | UINT32
1696 | 2 | Vt, Phase C-N | UINT32
1698 | 2 | Vt, Phase A-B | UINT32
1700 | 2 | Vt, Phase B-C | UINT32
1702 | 2 | Vt, Phase C-A | UINT32
1704 | 2 | +Qh, Total | SINT32
1706 | 2 | +Qh, Phase A | SINT32
1708 | 2 | +Qh, Phase B | SINT32
1710 | 2 | +Qh, Phase C | SINT32
1712 | 2 | -Qh, Total | SINT32
1714 | 2 | -Qh, Phase A | SINT32
1716 | 2 | -Qh, Phase B | SINT32
1718 | 2 | -Qh, Phase C | SINT32
1720 | 2 | V2t Phase A | UINT32
1722 | 2 | V2t Phase B | UINT32
1724 | 2 | V2t Phase C | UINT32
1726 | 2 | V2t Phase A-B | UINT32
1728 | 2 | V2t Phase B-C | UINT32
1730 | 2 | V2t Phase C-A | UINT32
1732 | 2 | I2t Phase A | UINT32
1734 | 2 | I2t Phase B | UINT32
1736 | 2 | I2t Phase C | UINT32
1738 | 2 | I2t Phase N | UINT32
1740 | 2 | Wh Net unsigned | UINT32
1742 | 2 | VARh Net unsigned | UINT32
1744 | 2 | V2t L-N 3 phaseTotal | UINT32
1746 | 2 | V2t L-L 3 Phase Total | UINT32
1748 | 2 | I2t 3 phase Total | UINT32
1997 | 3 | Demand Interval End Timestamp | TSTAMP
2000 | 2 | I A, Average | FLOAT
2002 | 2 | I B, Average | FLOAT
2004 | 2 | I C, Average | FLOAT
2006 | 2 | W, (Q1+Q4), Total, Average | FLOAT
2008 | 2 | VAR, (Q1+Q2), Total, Average | FLOAT
2010 | 2 | W, (Q2+Q3), Total, Average | FLOAT
2012 | 2 | VAR, (Q3+Q4), Total, Average | FLOAT
2014 | 2 | VA, Total, Average | FLOAT
2016 | 2 | PF, (Q1+Q4), Total, Average | FLOAT
2018 | 2 | PF, (Q2+Q3), Total, Average | FLOAT
2020 | 2 | I Neutral, Average | FLOAT
2022 | 2 | W, (Q1+Q4), Phase A, Average | FLOAT
2024 | 2 | W, (Q1+Q4), Phase B, Average | FLOAT
2026 | 2 | W, (Q1+Q4), Phase C, Average | FLOAT
2028 | 2 | VAR, (Q1+Q2), Phase A, Average | FLOAT
2030 | 2 | VAR, (Q1+Q2), Phase B, Average | FLOAT
2032 | 2 | VAR, (Q1+Q2), Phase C, Average | FLOAT
2034 | 2 | W, (Q2+Q3), Phase A, Average | FLOAT
2036 | 2 | W, (Q2+Q3), Phase B, Average | FLOAT
2038 | 2 | W, (Q2+Q3), Phase C, Average | FLOAT
2040 | 2 | VAR, (Q3+Q4), Phase A, Average | FLOAT
2042 | 2 | VAR, (Q3+Q4), Phase B, Average | FLOAT
2044 | 2 | VAR, (Q3+Q4), Phase C, Average | FLOAT
2046 | 2 | VA, Phase A, Average | FLOAT
2048 | 2 | VA, Phase B, Average | FLOAT
2050 | 2 | VA, Phase C, Average | FLOAT
2052 | 2 | PF, (Q1+Q4), Phase A, Average | FLOAT
2054 | 2 | PF, (Q1+Q4) Phase B, Average | FLOAT
2056 | 2 | PF, (Q1+Q4), Phase C, Average | FLOAT
2058 | 2 | PF, (Q2+Q3), Phase A, Average | FLOAT
2060 | 2 | PF, (Q2+Q3), Phase B, Average | FLOAT
2062 | 2 | PF, (Q2+Q3), Phase C, Average | FLOAT
2064 | 2 | W, (Q1), Total, Average | FLOAT
2066 | 2 | VAR, (Q1), Total, Average | FLOAT
2068 | 2 | VA, (Q1), Total, Average | FLOAT
2070 | 2 | W, (Q1), Phase A, Average | FLOAT
2072 | 2 | W, (Q1), Phase B, Average | FLOAT
2074 | 2 | W, (Q1), Phase C, Average | FLOAT
2076 | 2 | VAR, (Q1), Phase A, Average | FLOAT
2078 | 2 | VAR, (Q1), Phase B, Average | FLOAT
2080 | 2 | VAR, (Q1), Phase C, Average | FLOAT
2082 | 2 | VA, (Q1), Phase A, Average | FLOAT
2084 | 2 | VA, (Q1), Phase B, Average | FLOAT
2086 | 2 | VA, (Q1), Phase C, Average | FLOAT
2088 | 2 | W, (Q2), Total, Average | FLOAT
2090 | 2 | VAR, (Q2), Total, Average | FLOAT
2092 | 2 | VA, (Q2), Total, Average | FLOAT
2094 | 2 | W, (Q2), Phase A, Average | FLOAT
2096 | 2 | W, (Q2), Phase B, Average | FLOAT
2098 | 2 | W, (Q2), Phase C, Average | FLOAT
2100 | 2 | VAR, (Q2), Phase A, Average | FLOAT
2102 | 2 | VAR, (Q2), Phase B, Average | FLOAT
2104 | 2 | VAR, (Q2), Phase C, Average | FLOAT
2106 | 2 | VA, (Q2), Phase A, Average | FLOAT
2108 | 2 | VA, (Q2), Phase B, Average | FLOAT
2110 | 2 | VA, (Q2), Phase C, Average | FLOAT
2112 | 2 | W, (Q3), Total, Average | FLOAT
2114 | 2 | VAR, (Q3), Total, Average | FLOAT
2116 | 2 | VA, (Q3), Total, Average | FLOAT
2118 | 2 | W, (Q3), Phase A, Average | FLOAT
2120 | 2 | W, (Q3), Phase B, Average | FLOAT
2122 | 2 | W, (Q3), Phase C, Average | FLOAT
2124 | 2 | VAR, (Q3), Phase A, Average | FLOAT
2126 | 2 | VAR, (Q3), Phase B, Average | FLOAT
2128 | 2 | VAR, (Q3), Phase C, Average | FLOAT
2130 | 2 | VA, (Q3), Phase A, Average | FLOAT
2132 | 2 | VA, (Q3), Phase B, Average | FLOAT
2134 | 2 | VA, (Q3), Phase C, Average | FLOAT
2136 | 2 | W, (Q4), Total, Average | FLOAT
2138 | 2 | VAR, (Q4), Total, Average | FLOAT
2140 | 2 | VA, (Q4), Total, Average | FLOAT
2142 | 2 | W, (Q4), Phase A, Average | FLOAT
2144 | 2 | W, (Q4), Phase B, Average | FLOAT
2146 | 2 | W, (Q4), Phase C, Average | FLOAT
2148 | 2 | VAR, (Q4), Phase A, Average | FLOAT
2150 | 2 | VAR, (Q4), Phase B, Average | FLOAT
2152 | 2 | VAR, (Q4), Phase C, Average | FLOAT
2154 | 2 | VA, (Q4), Phase A, Average | FLOAT
2156 | 2 | VA, (Q4), Phase B, Average | FLOAT
2158 | 2 | VA, (Q4), Phase C, Average | FLOAT
2160 | 2 | VA, (Q1+Q4), Total, Average | FLOAT
2162 | 2 | VA, (Q1+Q4), Phase A, Average | FLOAT
2164 | 2 | VA, (Q1+Q4), Phase B, Average | FLOAT
2166 | 2 | VA, (Q1+Q4), Phase C, Average | FLOAT
2168 | 2 | VA, (Q2+Q3),Total, Average | FLOAT
2170 | 2 | VA, (Q2+Q3), Phase A, Average | FLOAT
2172 | 2 | VA, (Q2+Q3), Phase B, Average | FLOAT
2174 | 2 | VA, (Q2+Q3), Phase C, Average | FLOAT
2176 | 2 | V A-N, Average, Average | FLOAT
2178 | 2 | V B-N, Average, Average | FLOAT
2180 | 2 | V C-N, Average, Average | FLOAT
2182 | 2 | V A-B, Average, Average | FLOAT
2184 | 2 | V B-C, Average, Average | FLOAT
2186 | 2 | V C-A, Average, Average | FLOAT
2188 | 2 | +Q, Total, Average | FLOAT
2190 | 2 | +Q, Phase A, Average | FLOAT
2192 | 2 | +Q, Phase B, Average | FLOAT
2194 | 2 | +Q, Phase C, Average | FLOAT
2196 | 2 | -Q, Total, Average | FLOAT
2198 | 2 | -Q, Phase A, Average | FLOAT
2200 | 2 | -Q, Phase B, Average | FLOAT
2202 | 2 | -Q, Phase C, Average | FLOAT
2204 | 2 | Aggregator 1, Average | FLOAT
2206 | 2 | Aggregator 2, Average | FLOAT
2208 | 2 | Aggregator 3, Average | FLOAT
2210 | 2 | Aggregator 4, Average | FLOAT
2212 | 2 | Option card 1 input accumulator 1, Average | FLOAT
2214 | 2 | Option card 1 input accumulator 2, Average | FLOAT
2216 | 2 | Option card 1 input accumulator 3, Average | FLOAT
2218 | 2 | Option card 1 input accumulator 4, Average | FLOAT
2220 | 2 | Option card 2 input accumulator 1, Average | FLOAT
2222 | 2 | Option card 2 input accumulator 2, Average | FLOAT
2224 | 2 | Option card 2 input accumulator 3, Average | FLOAT
2226 | 2 | Option card 2 input accumulator 4, Average | FLOAT
3000 | 2 | W, Total | FLOAT
3002 | 2 | VAR, Total | FLOAT
3004 | 2 | VA, Total | FLOAT
3006 | 2 | PF, Total | FLOAT
3008 | 2 | W, Phase A | FLOAT
3010 | 2 | W, Phase B | FLOAT
3012 | 2 | W, Phase C | FLOAT
3014 | 2 | VAR, Phase A | FLOAT
3016 | 2 | VAR, Phase B | FLOAT
3018 | 2 | VAR, Phase C | FLOAT
3020 | 2 | VA, Phase A | FLOAT
3022 | 2 | VA, Phase B | FLOAT
3024 | 2 | VA, Phase C | FLOAT
3026 | 2 | PF, Phase A | FLOAT
3028 | 2 | PF, Phase B | FLOAT
3030 | 2 | PF, Phase C | FLOAT
3032 | 2 | Wh, (Q1+Q4) | SINT32
3034 | 2 | Wh, (Q2+Q3) | SINT32
3036 | 2 | Wh, Net | SINT32
3038 | 2 | Wh, Total | SINT32
3040 | 2 | VARh, (Q1+Q2) | SINT32
3042 | 2 | VARh, (Q3+Q4) | SINT32
3044 | 2 | VARh, Net | SINT32
3046 | 2 | VARh, Total | SINT32
3048 | 2 | VAh, Total | SINT32
3050 | 2 | Wh, (Q1+Q4), Phase A | SINT32
3052 | 2 | Wh, (Q1+Q4), Phase B | SINT32
3054 | 2 | Wh, (Q1+Q4), Phase C | SINT32
3056 | 2 | Wh, (Q2+Q3), Phase A | SINT32
3058 | 2 | Wh, (Q2+Q3), Phase B | SINT32
3060 | 2 | Wh, (Q2+Q3), Phase C | SINT32
3062 | 2 | Wh, Net, Phase A | SINT32
3064 | 2 | Wh, Net, Phase B | SINT32
3066 | 2 | Wh, Net, Phase C | SINT32
3068 | 2 | Wh, Total, Phase A | SINT32
3070 | 2 | Wh, Total, Phase B | SINT32
3072 | 2 | Wh, Total, Phase C | SINT32
3074 | 2 | VARh, (Q1+Q2), Phase A | SINT32
3076 | 2 | VARh, (Q1+Q2), Phase B | SINT32
3078 | 2 | VARh, (Q1+Q2), Phase C | SINT32
3080 | 2 | VARh, (Q3+Q4), Phase A | SINT32
3082 | 2 | VARh, (Q3+Q4), Phase B | SINT32
3084 | 2 | VARh, (Q3+Q4), Phase C | SINT32
3086 | 2 | VARh, Net, Phase A | SINT32
3088 | 2 | VARh, Net, Phase B | SINT32
3090 | 2 | VARh, Net, Phase C | SINT32
3092 | 2 | VARh, Total, Phase A | SINT32
3094 | 2 | VARh, Total, Phase B | SINT32
3096 | 2 | VARh, Total, Phase C | SINT32
3098 | 2 | VAh, Phase A | SINT32
3100 | 2 | VAh, Phase B | SINT32
3102 | 2 | VAh, Phase C | SINT32
3104 | 2 | Wh, (Q1), Total | SINT32
3106 | 2 | VARh, (Q1), Total | SINT32
3108 | 2 | VAh, (Q1), Total | SINT32
3110 | 2 | Wh, (Q1), Phase A | SINT32
3112 | 2 | Wh, (Q1), Phase B | SINT32
3114 | 2 | Wh, (Q1), Phase C | SINT32
3116 | 2 | VARh, (Q1), Phase A | SINT32
3118 | 2 | VARh, (Q1), Phase B | SINT32
3120 | 2 | VARh, (Q1), Phase C | SINT32
3122 | 2 | VAh, (Q1), Phase A | SINT32
3124 | 2 | VAh, (Q1), Phase B | SINT32
3126 | 2 | VAh, (Q1), Phase C | SINT32
3128 | 2 | Wh, (Q2), Total | SINT32
3130 | 2 | VARh, (Q2), Total | SINT32
3132 | 2 | VAh, (Q2), Total | SINT32
3134 | 2 | Wh, (Q2), Phase A | SINT32
3136 | 2 | Wh, (Q2), Phase B | SINT32
3138 | 2 | Wh, (Q2), Phase C | SINT32
3140 | 2 | VARh, (Q2), Phase A | SINT32
3142 | 2 | VARh, (Q2), Phase B | SINT32
3144 | 2 | VARh, (Q2), Phase C | SINT32
3146 | 2 | VAh, (Q2), Phase A | SINT32
3148 | 2 | VAh, (Q2), Phase B | SINT32
3150 | 2 | VAh, (Q2), Phase C | SINT32
3152 | 2 | Wh, (Q3), Total | SINT32
3154 | 2 | VARh, (Q3), Total | SINT32
3156 | 2 | VAh, (Q3), Total | SINT32
3158 | 2 | Wh, (Q3), Phase A | SINT32
3160 | 2 | Wh, (Q3), Phase B | SINT32
3162 | 2 | Wh, (Q3), Phase C | SINT32
3164 | 2 | VARh, (Q3), Phase A | SINT32
3166 | 2 | VARh, (Q3), Phase B | SINT32
3168 | 2 | VARh, (Q3), Phase C | SINT32
3170 | 2 | VAh, (Q3), Phase A | SINT32
3172 | 2 | VAh, (Q3), Phase B | SINT32
3174 | 2 | VAh, (Q3), Phase C | SINT32
3176 | 2 | Wh, (Q4), Total | SINT32
3178 | 2 | VARh, (Q4), Total | SINT32
3180 | 2 | VAh, (Q4), Total | SINT32
3182 | 2 | Wh, (Q4), Phase A | SINT32
3184 | 2 | Wh, (Q4), Phase B | SINT32
3186 | 2 | Wh, (Q4), Phase C | SINT32
3188 | 2 | VARh, (Q4), Phase A | SINT32
3190 | 2 | VARh, (Q4), Phase B | SINT32
3192 | 2 | VARh, (Q4), Phase C | SINT32
3194 | 2 | VAh, (Q4), Phase A | SINT32
3196 | 2 | VAh, (Q4), Phase B | SINT32
3198 | 2 | VAh, (Q4), Phase C | SINT32
3200 | 2 | VAh, (Q1+Q4), Total | SINT32
3202 | 2 | VAh, (Q1+Q4), Phase A | SINT32
3204 | 2 | VAh, (Q1+Q4), Phase B | SINT32
3206 | 2 | VAh, (Q1+Q4), Phase C | SINT32
3208 | 2 | VAh, (Q2+Q3), Total | SINT32
3210 | 2 | VAh, (Q2+Q3), Phase A | SINT32
3212 | 2 | VAh, (Q2+Q3), Phase B | SINT32
3214 | 2 | VAh, (Q2+Q3), Phase C | SINT32
3216 | 2 | Q, Total | FLOAT
3218 | 2 | Q, Phase A | FLOAT
3220 | 2 | Q, Phase B | FLOAT
3222 | 2 | Q, Phase C | FLOAT
3224 | 2 | +Qh, Total | SINT32
3226 | 2 | +Qh, Phase A | SINT32
3228 | 2 | +Qh, Phase B | SINT32
3230 | 2 | +Qh, Phase C | SINT32
3232 | 2 | -Qh, Total | SINT32
3234 | 2 | -Qh, Phase A | SINT32
3236 | 2 | -Qh, Phase B | SINT32
3238 | 2 | -Qh, Phase C | SINT32
4100 | 1 | Phasor Angle, I A - V A | SINT16
4101 | 1 | Phasor Angle, I B - V B | SINT16
4102 | 1 | Phasor Angle, I C - V C | SINT16
4103 | 1 | Phasor Angle, V A - VB | SINT16
4104 | 1 | Phasor Angle, V B - V C | SINT16
4105 | 1 | Phasor Angle, V C - V A | SINT16
5000 | 2 | Wh, (Q1+Q4) | SINT32
5002 | 2 | Wh, (Q2+Q3) | SINT32
5004 | 2 | ` | SINT32
5006 | 2 | Wh, Total | SINT32
5008 | 2 | VARh, (Q1+Q2) | SINT32
5010 | 2 | VARh, (Q3+Q4) | SINT32
5012 | 2 | VARh, Net | SINT32
5014 | 2 | VARh, Total | SINT32
5016 | 2 | VAh, Total | SINT32
5018 | 2 | Wh, (Q1+Q4), Phase A | SINT32
5020 | 2 | Wh, (Q1+Q4), Phase B | SINT32
5022 | 2 | Wh, (Q1+Q4), Phase C | SINT32
5024 | 2 | Wh, (Q2+Q3), Phase A | SINT32
5026 | 2 | Wh, (Q2+Q3), Phase B | SINT32
5028 | 2 | Wh, (Q2+Q3), Phase C | SINT32
5030 | 2 | Wh, Net, Phase A | SINT32
5032 | 2 | Wh, Net, Phase B | SINT32
5034 | 2 | Wh, Net, Phase C | SINT32
5036 | 2 | Wh, Total, Phase A | SINT32
5038 | 2 | Wh, Total, Phase B | SINT32
5040 | 2 | Wh, Total, Phase C | SINT32
5042 | 2 | VARh, (Q1+Q2), Phase A | SINT32
5044 | 2 | VARh, (Q1+Q2), Phase B | SINT32
5046 | 2 | VARh, (Q1+Q2), Phase C | SINT32
5048 | 2 | VARh, (Q3+Q4), Phase A | SINT32
5050 | 2 | VARh, (Q3+Q4), Phase B | SINT32
5052 | 2 | VARh, (Q3+Q4), Phase C | SINT32
5054 | 2 | VARh, Net, Phase A | SINT32
5056 | 2 | VARh, Net, Phase B | SINT32
5058 | 2 | VARh, Net, Phase C | SINT32
5060 | 2 | VARh, Total, Phase A | SINT32
5062 | 2 | VARh, Total, Phase B | SINT32
5064 | 2 | VARh, Total, Phase C | SINT32
5066 | 2 | VAh, Phase A | SINT32
5068 | 2 | VAh, Phase B | SINT32
5070 | 2 | VAh, Phase C | SINT32
5072 | 2 | Wh, (Q1), Total | SINT32
5074 | 2 | VARh, (Q1), Total | SINT32
5076 | 2 | VAh, (Q1), Total | SINT32
5078 | 2 | Wh, (Q1), Phase A | SINT32
5080 | 2 | Wh, (Q1), Phase B | SINT32
5082 | 2 | Wh, (Q1), Phase C | SINT32
5084 | 2 | VARh, (Q1), Phase A | SINT32
5086 | 2 | VARh, (Q1), Phase B | SINT32
5088 | 2 | VARh, (Q1), Phase C | SINT32
5090 | 2 | VAh, (Q1), Phase A | SINT32
5092 | 2 | VAh, (Q1), Phase B | SINT32
5094 | 2 | VAh, (Q1), Phase C | SINT32
5096 | 2 | Wh, (Q2), Total | SINT32
5098 | 2 | VARh, (Q2), Total | SINT32
5100 | 2 | VAh, (Q2), Total | SINT32
5102 | 2 | Wh, (Q2), Phase A | SINT32
5104 | 2 | Wh, (Q2), Phase B | SINT32
5106 | 2 | Wh, (Q2), Phase C | SINT32
5108 | 2 | VARh, (Q2), Phase A | SINT32
5110 | 2 | VARh, (Q2), Phase B | SINT32
5112 | 2 | VARh, (Q2), Phase C | SINT32
5114 | 2 | VAh, (Q2), Phase A | SINT32
5116 | 2 | VAh, (Q2), Phase B | SINT32
5118 | 2 | VAh, (Q2), Phase C | SINT32
5120 | 2 | Wh, (Q3), Total | SINT32
5122 | 2 | VARh, (Q3), Total | SINT32
5124 | 2 | VAh, (Q3), Total | SINT32
5126 | 2 | Wh, (Q3), Phase A | SINT32
5128 | 2 | Wh, (Q3), Phase B | SINT32
5130 | 2 | Wh, (Q3), Phase C | SINT32
5132 | 2 | VARh, (Q3), Phase A | SINT32
5134 | 2 | VARh, (Q3), Phase B | SINT32
5136 | 2 | VARh, (Q3), Phase C | SINT32
5138 | 2 | VAh, (Q3), Phase A | SINT32
5140 | 2 | VAh, (Q3), Phase B | SINT32
5142 | 2 | VAh, (Q3), Phase C | SINT32
5144 | 2 | Wh, (Q4), Total | SINT32
5146 | 2 | VARh, (Q4), Total | SINT32
5148 | 2 | VAh, (Q4), Total | SINT32
5150 | 2 | Wh, (Q4), Phase A | SINT32
5152 | 2 | Wh, (Q4), Phase B | SINT32
5154 | 2 | Wh, (Q4), Phase C | SINT32
5156 | 2 | VARh, (Q4), Phase A | SINT32
5158 | 2 | VARh, (Q4), Phase B | SINT32
5160 | 2 | VARh, (Q4), Phase C | SINT32
5162 | 2 | VAh, (Q4), Phase A | SINT32
5164 | 2 | VAh, (Q4), Phase B | SINT32
5166 | 2 | VAh, (Q4), Phase C | SINT32
5168 | 2 | VAh, (Q1+Q4), Total | SINT32
5170 | 2 | VAh, (Q1+Q4), Phase A | SINT32
5172 | 2 | VAh, (Q1+Q4), Phase B | SINT32
5174 | 2 | VAh, (Q1+Q4), Phase C | SINT32
5176 | 2 | VAh, (Q2+Q3), Total | SINT32
5178 | 2 | VAh, (Q2+Q3), Phase A | SINT32
5180 | 2 | VAh, (Q2+Q3), Phase B | SINT32
5182 | 2 | VAh, (Q2+Q3), Phase C | SINT32
5184 | 2 | It, Phase A | SINT32
5186 | 2 | It, Phase B | SINT32
5188 | 2 | It, Phase C | SINT32
5190 | 2 | It, Phase N | SINT32
5192 | 2 | Vt, Phase A-N | SINT32
5194 | 2 | Vt, Phase B-N | SINT32
5196 | 2 | Vt, Phase C-N | SINT32
5198 | 2 | Vt, Phase A-B | SINT32
5200 | 2 | Vt, Phase B-C | SINT32
5202 | 2 | Vt, Phase C-A | SINT32
5204 | 2 | +Qh, Total | SINT32
5206 | 2 | +Qh, Phase A | SINT32
5208 | 2 | +Qh, Phase B | SINT32
5210 | 2 | +Qh, Phase C | SINT32
5212 | 2 | -Qh, Total | SINT32
5214 | 2 | -Qh, Phase A | SINT32
5216 | 2 | -Qh, Phase B | SINT32
5218 | 2 | -Qh, Phase C | SINT32
5220 | 2 | Aggregator 1 | SINT32
5222 | 2 | Aggregator 2 | SINT32
5224 | 2 | Aggregator 3 | SINT32
5226 | 2 | Aggregator 4 | SINT32
5228 | 2 | Option card 1 input accumulator 1 | UINT32
5230 | 2 | Option card 1 input accumulator 2 | UINT32
5232 | 2 | Option card 1 input accumulator 3 | UINT32
5234 | 2 | Option card 1 input accumulator 4 | UINT32
5236 | 2 | Option card 2 input accumulator 1 | UINT32
5238 | 2 | Option card 2 input accumulator 2 | UINT32
5240 | 2 | Option card 2 input accumulator 3 | UINT32
5242 | 2 | Option card 2 input accumulator 4 | UINT32
5500 | 2 | Wh, (Q1+Q4) | SINT32
5502 | 2 | Wh, (Q2+Q3) | SINT32
5504 | 2 | Wh, Net | SINT32
5506 | 2 | Wh, Total | SINT32
5508 | 2 | VARh, (Q1+Q2) | SINT32
5510 | 2 | VARh, (Q3+Q4) | SINT32
5512 | 2 | VARh, Net | SINT32
5514 | 2 | VARh, Total | SINT32
5516 | 2 | VAh, Total | SINT32
5518 | 2 | Wh, (Q1+Q4), Phase A | SINT32
5520 | 2 | Wh, (Q1+Q4), Phase B | SINT32
5522 | 2 | Wh, (Q1+Q4), Phase C | SINT32
5524 | 2 | Wh, (Q2+Q3), Phase A | SINT32
5526 | 2 | Wh, (Q2+Q3), Phase B | SINT32
5528 | 2 | Wh, (Q2+Q3), Phase C | SINT32
5530 | 2 | Wh, Net, Phase A | SINT32
5532 | 2 | Wh, Net, Phase B | SINT32
5534 | 2 | Wh, Net, Phase C | SINT32
5536 | 2 | Wh, Total, Phase A | SINT32
5538 | 2 | Wh, Total, Phase B | SINT32
5540 | 2 | Wh, Total, Phase C | SINT32
5542 | 2 | VARh, (Q1+Q2), Phase A | SINT32
5544 | 2 | VARh, (Q1+Q2), Phase B | SINT32
5546 | 2 | VARh, (Q1+Q2), Phase C | SINT32
5548 | 2 | VARh, (Q3+Q4), Phase A | SINT32
5550 | 2 | VARh, (Q3+Q4), Phase B | SINT32
5552 | 2 | VARh, (Q3+Q4), Phase C | SINT32
5554 | 2 | VARh, Net, Phase A | SINT32
5556 | 2 | VARh, Net, Phase B | SINT32
5558 | 2 | VARh, Net, Phase C | SINT32
5560 | 2 | VARh, Total, Phase A | SINT32
5562 | 2 | VARh, Total, Phase B | SINT32
5564 | 2 | VARh, Total, Phase C | SINT32
5566 | 2 | VAh, Phase A | SINT32
5568 | 2 | VAh, Phase B | SINT32
5570 | 2 | VAh, Phase C | SINT32
5572 | 2 | Wh, (Q1), Total | SINT32
5574 | 2 | VARh, (Q1), Total | SINT32
5576 | 2 | VAh, (Q1), Total | SINT32
5578 | 2 | Wh, (Q1), Phase A | SINT32
5580 | 2 | Wh, (Q1), Phase B | SINT32
5582 | 2 | Wh, (Q1), Phase C | SINT32
5584 | 2 | VARh, (Q1), Phase A | SINT32
5586 | 2 | VARh, (Q1), Phase B | SINT32
5588 | 2 | VARh, (Q1), Phase C | SINT32
5590 | 2 | VAh, (Q1), Phase A | SINT32
5592 | 2 | VAh, (Q1), Phase B | SINT32
5594 | 2 | VAh, (Q1), Phase C | SINT32
5596 | 2 | Wh, (Q2), Total | SINT32
5598 | 2 | VARh, (Q2), Total | SINT32
5600 | 2 | VAh, (Q2), Total | SINT32
5602 | 2 | Wh, (Q2), Phase A | SINT32
5604 | 2 | Wh, (Q2), Phase B | SINT32
5606 | 2 | Wh, (Q2), Phase C | SINT32
5608 | 2 | VARh, (Q2), Phase A | SINT32
5610 | 2 | VARh, (Q2), Phase B | SINT32
5612 | 2 | VARh, (Q2), Phase C | SINT32
5614 | 2 | VAh, (Q2), Phase A | SINT32
5616 | 2 | VAh, (Q2), Phase B | SINT32
5618 | 2 | VAh, (Q2), Phase C | SINT32
5620 | 2 | Wh, (Q3), Total | SINT32
5622 | 2 | VARh, (Q3), Total | SINT32
5624 | 2 | VAh, (Q3), Total | SINT32
5626 | 2 | Wh, (Q3), Phase A | SINT32
5628 | 2 | Wh, (Q3), Phase B | SINT32
5630 | 2 | Wh, (Q3), Phase C | SINT32
5632 | 2 | VARh, (Q3), Phase A | SINT32
5634 | 2 | VARh, (Q3), Phase B | SINT32
5636 | 2 | VARh, (Q3), Phase C | SINT32
5638 | 2 | VAh, (Q3), Phase A | SINT32
5640 | 2 | VAh, (Q3), Phase B | SINT32
5642 | 2 | VAh, (Q3), Phase C | SINT32
5644 | 2 | Wh, (Q4), Total | SINT32
5646 | 2 | VARh, (Q4), Total | SINT32
5648 | 2 | VAh, (Q4), Total | SINT32
5650 | 2 | Wh, (Q4), Phase A | SINT32
5652 | 2 | Wh, (Q4), Phase B | SINT32
5654 | 2 | Wh, (Q4), Phase C | SINT32
5656 | 2 | VARh, (Q4), Phase A | SINT32
5658 | 2 | VARh, (Q4), Phase B | SINT32
5660 | 2 | VARh, (Q4), Phase C | SINT32
5662 | 2 | VAh, (Q4), Phase A | SINT32
5664 | 2 | VAh, (Q4), Phase B | SINT32
5666 | 2 | VAh, (Q4), Phase C | SINT32
5668 | 2 | VAh, (Q1+Q4), Total | SINT32
5670 | 2 | VAh, (Q1+Q4), Phase A | SINT32
5672 | 2 | VAh, (Q1+Q4), Phase B | SINT32
5674 | 2 | VAh, (Q1+Q4), Phase C | SINT32
5676 | 2 | VAh, (Q2+Q3), Total | SINT32
5678 | 2 | VAh, (Q2+Q3), Phase A | SINT32
5680 | 2 | VAh, (Q2+Q3), Phase B | SINT32
5682 | 2 | VAh, (Q2+Q3), Phase C | SINT32
5684 | 2 | It, Phase A | SINT32
5686 | 2 | It, Phase B | SINT32
5688 | 2 | It, Phase C | SINT32
5690 | 2 | It, Phase N | SINT32
5692 | 2 | Vt, Phase A-N | SINT32
5694 | 2 | Vt, Phase B-N | SINT32
5696 | 2 | Vt, Phase C-N | SINT32
5698 | 2 | Vt, Phase A-B | SINT32
5700 | 2 | Vt, Phase B-C | SINT32
5702 | 2 | Vt, Phase C-A | SINT32
5704 | 2 | +Qh, Total | SINT32
5706 | 2 | +Qh, Phase A | SINT32
5708 | 2 | +Qh, Phase B | SINT32
5710 | 2 | +Qh, Phase C | SINT32
5712 | 2 | -Qh, Total | SINT32
5714 | 2 | -Qh, Phase A | SINT32
5716 | 2 | -Qh, Phase B | SINT32
5718 | 2 | -Qh, Phase C | SINT32
5889 | 512 | Custom Modbus Map Data | UINT16
7948 | 2 | Maximum W, (Q1+Q4), Total, prior to Demand Reset | FLOAT
7950 | 2 | Maximum W, (Q2+Q3), Total, prior to Demand Reset | FLOAT
7952 | 2 | Maximum VAR, (Q1+Q2), Total, prior to Demand Reset | FLOAT
7954 | 2 | Maximum VAR, (Q3+Q4), Total, prior to Demand Reset | FLOAT
7956 | 2 | Maximum VA, Total , prior to Demand Reset | FLOAT
7958 | 3 | Maximum W, (Q1+Q4), Total, Timestamp, prior to Demand Reset | TSTAMP
7961 | 3 | Maximum W, (Q2+Q3), Total, Timestamp, prior to Demand Reset | TSTAMP
7964 | 3 | Maximum VAR, (Q1+Q2), Total, Timestamp, prior to Demand Reset | TSTAMP
7967 | 3 | Maximum VAR, (Q3+Q4), Total,Timestamp, prior to Demand Reset | TSTAMP
7970 | 3 | Maximum VA, Total , Timestamp, prior to Demand Reset | TSTAMP
7973 | 3 | Demand Last Reset Timestamp | TSTAMP
7976 | 2 | V A-N, previous Demand interval Short Term Minimum | FLOAT
7978 | 2 | V B-N, previous Demand interval Short Term Minimum | FLOAT
7980 | 2 | V C-N, previous Demand interval Short Term Minimum | FLOAT
7982 | 2 | V A-B, previous Demand interval Short Term Minimum | FLOAT
7984 | 2 | V B-C, previous Demand interval Short Term Minimum | FLOAT
7986 | 2 | V C-A, previous Demand interval Short Term Minimum | FLOAT
7988 | 2 | V A-N, Short Term Minimum | FLOAT
7990 | 2 | V B-N, Short Term Minimum | FLOAT
7992 | 2 | V C-N, Short Term Minimum | FLOAT
7994 | 2 | V A-B, Short Term Minimum | FLOAT
7996 | 2 | V B-C, Short Term Minimum | FLOAT
7998 | 2 | V C-A, Short Term Minimum | FLOAT
8000 | 2 | V A-N, Minimum | FLOAT
8002 | 2 | V B-N, Minimum | FLOAT
8004 | 2 | V C-N, Minimum | FLOAT
8006 | 2 | V A-B, Minimum | FLOAT
8008 | 2 | V B-C, Minimum | FLOAT
8010 | 2 | V C-A, Minimum | FLOAT
8012 | 2 | I A, Minimum Average Demand | FLOAT
8014 | 2 | I B, Minimum Average Demand | FLOAT
8016 | 2 | I C, Minimum Average Demand | FLOAT
8018 | 2 | W, (Q1+Q4), Total, Minimum Average Demand | FLOAT
8020 | 2 | VAR, (Q1+Q2), Total, Minimum Average Demand | FLOAT
8022 | 2 | W, (Q2+Q3), Total, Minimum Average Demand | FLOAT
8024 | 2 | VAR, (Q3+Q4), Total, Minimum Average Demand | FLOAT
8026 | 2 | VA, Total, Minimum Average Demand | FLOAT
8028 | 2 | PF, (Q1+Q4), Total, Minimum Average Demand | FLOAT
8030 | 2 | PF, (Q2+Q3), Total, Minimum Average Demand | FLOAT
8032 | 2 | Frequency, Minimum | FLOAT
8034 | 2 | Neutral Current, Minimum Average Demand | FLOAT
8036 | 2 | W, (Q1+Q4), Phase A, Minimum Average Demand | FLOAT
8038 | 2 | W, (Q1+Q4), Phase B, Minimum Average Demand | FLOAT
8040 | 2 | W, (Q1+Q4), Phase C, Minimum Average Demand | FLOAT
8042 | 2 | VAR, (Q1+Q2), Phase A, Minimum Average Demand | FLOAT
8044 | 2 | VAR, (Q1+Q2), Phase B, Minimum Average Demand | FLOAT
8046 | 2 | VAR, (Q1+Q2), Phase C, Minimum Average Demand | FLOAT
8048 | 2 | W, (Q2+Q3), Phase A, Minimum Average Demand | FLOAT
8050 | 2 | W, (Q2+Q3), Phase B, Minimum Average Demand | FLOAT
8052 | 2 | W, (Q2+Q3), Phase C, Minimum Average Demand | FLOAT
8054 | 2 | VAR, (Q3+Q4), Phase A, Minimum Average Demand | FLOAT
8056 | 2 | VAR, (Q3+Q4), Phase B, Minimum Average Demand | FLOAT
8058 | 2 | VAR, (Q3+Q4), Phase C, Minimum Average Demand | FLOAT
8060 | 2 | VA, Phase A, Minimum Average Demand | FLOAT
8062 | 2 | VA, Phase B, Minimum Average Demand | FLOAT
8064 | 2 | VA, Phase C, Minimum Average Demand | FLOAT
8066 | 2 | PF, (Q1+Q4), Phase A, Minimum Average Demand | FLOAT
8068 | 2 | PF, (Q1+Q4), Phase B, Minimum Average Demand | FLOAT
8070 | 2 | PF, (Q1+Q4), Phase C, Minimum Average Demand | FLOAT
8072 | 2 | PF, (Q2+Q3), Phase A, Minimum Average Demand | FLOAT
8074 | 2 | PF, (Q2+Q3), Phase B, Minimum Average Demand | FLOAT
8076 | 2 | PF, (Q2+Q3), Phase C, Minimum Average Demand | FLOAT
8078 | 1 | V A-N, %THD, Minimum | UINT16
8079 | 1 | V B-N, %THD, Minimum | UINT16
8080 | 1 | V C-N, %THD, Minimum | UINT16
8081 | 1 | I A, %THD, Minimum | UINT16
8082 | 1 | I B, %THD, Minimum | UINT16
8083 | 1 | I C, %THD, Minimum | UINT16
8084 | 2 | Symmetrical Component Magnitude, 0 Seq, Minimum | FLOAT
8086 | 2 | Symmetrical Component Magnitude, + Seq, Minimum | FLOAT
8088 | 2 | Symmetrical Component Magnitude, - Seq, Minimum | FLOAT
8090 | 1 | Symmetrical Component Phase, 0 Seq, Minimum | SINT16
8091 | 1 | Symmetrical Component Phase, + Seq, Minimum | SINT16
8092 | 1 | Symmetrical Component Phase, - Seq, Minimum | SINT16
8093 | 1 | Unbalance, 0 sequence, Minimum | UINT16
8094 | 1 | Unbalance, -sequence, Minimum | UINT16
8095 | 1 | Current Unbalance, Minimum | UINT16
8096 | 2 | W, (Q1), Total, Minimum Average Demand | FLOAT
8098 | 2 | VAR, (Q1), Total, Minimum Average Demand | FLOAT
8100 | 2 | VA, (Q1), Total, Minimum Average Demand | FLOAT
8102 | 2 | W, (Q1), Phase A, Minimum Average Demand | FLOAT
8104 | 2 | W, (Q1), Phase B, Minimum Average Demand | FLOAT
8106 | 2 | W, (Q1), Phase C, Minimum Average Demand | FLOAT
8108 | 2 | AR, (Q1), Phase A, Minimum Average Demand | FLOAT
8110 | 2 | VAR, (Q1), Phase B, Minimum Average Demand | FLOAT
8112 | 2 | VAR, (Q1), Phase C, Minimum Average Demand | FLOAT
8114 | 2 | VA, (Q1), Phase A, Minimum Average Demand | FLOAT
8116 | 2 | VA, (Q1), Phase B, Minimum Average Demand | FLOAT
8118 | 2 | VA, (Q1), Phase C, Minimum Average Demand | FLOAT
8120 | 2 | W, (Q2), Total, Minimum Average Demand | FLOAT
8122 | 2 | VAR, (Q2), Total, Minimum Average Demand | FLOAT
8124 | 2 | VA, (Q2), Total, Minimum Average Demand | FLOAT
8126 | 2 | W, (Q2), Phase A, Minimum Average Demand | FLOAT
8128 | 2 | W, (Q2), Phase B, Minimum Average Demand | FLOAT
8130 | 2 | W, (Q2), Phase C, Minimum Average Demand | FLOAT
8132 | 2 | VAR, (Q2), Phase A, Minimum Average Demand | FLOAT
8134 | 2 | VAR, (Q2), Phase B, Minimum Average Demand | FLOAT
8136 | 2 | VAR, (Q2), Phase C, Minimum Average Demand | FLOAT
8138 | 2 | VA, (Q2), Phase A, Minimum Average Demand | FLOAT
8140 | 2 | VA, (Q2), Phase B, Minimum Average Demand | FLOAT
8142 | 2 | VA, (Q2), Phase C, Minimum Average Demand | FLOAT
8144 | 2 | W, (Q3), Total, Minimum Average Demand | FLOAT
8146 | 2 | VAR, (Q3), Total, Minimum Average Demand | FLOAT
8148 | 2 | VA, (Q3), Total, Minimum Average Demand | FLOAT
8150 | 2 | W, (Q3), Phase A, Minimum Average Demand | FLOAT
8152 | 2 | W, (Q3), Phase B, Minimum Average Demand | FLOAT
8154 | 2 | W, (Q3), Phase C, Minimum Average Demand | FLOAT
8156 | 2 | VAR, (Q3), Phase A, Minimum Average Demand | FLOAT
8158 | 2 | VAR, (Q3), Phase B, Minimum Average Demand | FLOAT
8160 | 2 | VAR, (Q3), Phase C, Minimum Average Demand | FLOAT
8162 | 2 | VA, (Q3), Phase A, Minimum Average Demand | FLOAT
8164 | 2 | VA, (Q3), Phase B, Minimum Average Demand | FLOAT
8166 | 2 | VA, (Q3), Phase C, Minimum Average Demand | FLOAT
8168 | 2 | W, (Q4), Total, Minimum Average Demand | FLOAT
8170 | 2 | VAR, (Q4), Total, Minimum Average Demand | FLOAT
8172 | 2 | VA, (Q4), Total, Minimum Average Demand | FLOAT
8174 | 2 | W, (Q4), Phase A, Minimum Average Demand | FLOAT
8176 | 2 | W, (Q4), Phase B, Minimum Average Demand | FLOAT
8178 | 2 | W, (Q4), Phase C, Minimum Average Demand | FLOAT
8180 | 2 | VAR, (Q4), Phase A, Minimum Average Demand | FLOAT
8182 | 2 | VAR, (Q4), Phase B, Minimum Average Demand | FLOAT
8184 | 2 | VAR, (Q4), Phase C, Minimum Average Demand | FLOAT
8186 | 2 | VA, (Q4), Phase A, Minimum Average Demand | FLOAT
8188 | 2 | VA, (Q4), Phase B, Minimum Average Demand | FLOAT
8190 | 2 | VA, (Q4), Phase C, Minimum Average Demand | FLOAT
8192 | 2 | VA (Q1+Q4),Total,Minimum Average Demand | FLOAT
8194 | 2 | VA (Q1+Q4),Phase A,Minimum Average Demand | FLOAT
8196 | 2 | VA (Q1+Q4),Phase B,Minimum Average Demand | FLOAT
8198 | 2 | VA (Q1+Q4),Phase C,Minimum Average Demand | FLOAT
8200 | 2 | VA (Q2+Q3),Total,Minimum Average Demand | FLOAT
8202 | 2 | VA (Q2+Q3),Phase A,Minimum Average Demand | FLOAT
8204 | 2 | VA (Q2+Q3),Phase B,Minimum Average Demand | FLOAT
8206 | 2 | VA (Q2+Q3),Phase C,Minimum Average Demand | FLOAT
8208 | 2 | V A-N, Minimum Average Demand | FLOAT
8210 | 2 | V B-N, Minimum Average Demand | FLOAT
8212 | 2 | V C-N, Minimum Average Demand | FLOAT
8214 | 2 | V A-B, Minimum Average Demand | FLOAT
8216 | 2 | V B-C, Minimum Average Demand | FLOAT
8218 | 2 | V C-A, Minimum Average Demand | FLOAT
8220 | 1 | I A, %TDD, Minimum | UINT16
8221 | 1 | I B, %TDD, Minimum | UINT16
8222 | 1 | I C, %TDD, Minimum | UINT16
8223 | 1 | I A, K-factor, Minimum | UINT16
8224 | 1 | I B, K-factor, Minimum | UINT16
8225 | 1 | I C, K-factor, Minimum | UINT16
8226 | 2 | +Q,Total, Minimum Average Demand | FLOAT
8228 | 2 | +Q,Phase A, Minimum Average Demand | FLOAT
8230 | 2 | +Q,Phase Minimum Average Demand | FLOAT
8232 | 2 | +Q,Phase C, Minimum Average Demand | FLOAT
8234 | 2 | -Q,Total, Minimum Average Demand | FLOAT
8236 | 2 | -Q,Phase A, Minimum Average Demand | FLOAT
8238 | 2 | -Q,Phase Minimum Average Demand | FLOAT
8240 | 2 | -Q,Phase C, Minimum Average Demand | FLOAT
8242 | 2 | Aggregator 1, Minimum Average Demand | FLOAT
8244 | 2 | Aggregator 2, Minimum Average Demand | FLOAT
8246 | 2 | Aggregator 3, Minimum Average Demand | FLOAT
8248 | 2 | Aggregator 4, Minimum Average Demand | FLOAT
8250 | 2 | Option card 1 input accumulator 1, Minimum Average Demand | FLOAT
8252 | 2 | Option card 1 input accumulator 2, Minimum Average Demand | FLOAT
8254 | 2 | Option card 1 input accumulator 3, Minimum Average Demand | FLOAT
8256 | 2 | Option card 1 input accumulator 4, Minimum Average Demand | FLOAT
8258 | 2 | Option card 2 input accumulator 1, Minimum Average Demand | FLOAT
8260 | 2 | Option card 2 input accumulator 2, Minimum Average Demand | FLOAT
8262 | 2 | Option card 2 input accumulator 3, Minimum Average Demand | FLOAT
8264 | 2 | Option card 2 input accumulator 4, Minimum Average Demand | FLOAT
8400 | 3 | V A-N, Minimum Timestamp | TSTAMP
8403 | 3 | V B-N, Minimum Timestamp | TSTAMP
8406 | 3 | V C-N, Minimum Timestamp | TSTAMP
8409 | 3 | V A-B, Minimum Timestamp | TSTAMP
8412 | 3 | V B-C, Minimum Timestamp | TSTAMP
8415 | 3 | V C-A, Minimum Timestamp | TSTAMP
8418 | 3 | I A, Minimum Average Demand Timestamp | TSTAMP
8421 | 3 | I B, Minimum Average Demand Timestamp | TSTAMP
8424 | 3 | I C, Minimum Average Demand Timestamp | TSTAMP
8427 | 3 | W, (Q1+Q4), Total, Minimum Average Demand Timestamp | TSTAMP
8430 | 3 | VAR, (Q1+Q2), Total, Minimum Average Demand Timestamp | TSTAMP
8433 | 3 | W, (Q2+Q3), Total, Minimum Average Demand Timestamp | TSTAMP
8436 | 3 | VAR, (Q3+Q4), Total, Minimum Average Demand Timestamp | TSTAMP
8439 | 3 | VA, Total, Minimum Average Demand Timestamp | TSTAMP
8442 | 3 | PF, (Q1+Q4), Total, Minimum Average Demand Timestamp | TSTAMP
8445 | 3 | PF, (Q2+Q3), Total, Minimum Average Demand Timestamp | TSTAMP
8448 | 3 | Frequency, Minimum Timestamp | TSTAMP
8451 | 3 | Neutral Current, Minimum Average Demand Timestamp | TSTAMP
8454 | 3 | W, (Q1+Q4), Phase A, Minimum Average Demand Timestamp | TSTAMP
8457 | 3 | W, (Q1+Q4), Phase B, Minimum Average Demand Timestamp | TSTAMP
8460 | 3 | W, (Q1+Q4), Phase C, Minimum Average Demand Timestamp | TSTAMP
8463 | 3 | VAR, (Q1+Q2), Phase A, Minimum Average Demand Timestamp | TSTAMP
8466 | 3 | VAR, (Q1+Q2), Phase B, Minimum Average Demand Timestamp | TSTAMP
8469 | 3 | VAR, (Q1+Q2), Phase C, Minimum Average Demand Timestamp | TSTAMP
8472 | 3 | W, (Q2+Q3), Phase A, Minimum Average Demand Timestamp | TSTAMP
8475 | 3 | W, (Q2+Q3), Phase B, Minimum Average Demand Timestamp | TSTAMP
8478 | 3 | W, (Q2+Q3), Phase C, Minimum Average Demand Timestamp | TSTAMP
8481 | 3 | VAR, (Q3+Q4), Phase A, Minimum Average Demand Timestamp | TSTAMP
8484 | 3 | VAR, (Q3+Q4), Phase B, Minimum Average Demand Timestamp | TSTAMP
8487 | 3 | VAR, (Q3+Q4), Phase C, Minimum Average Demand Timestamp | TSTAMP
8490 | 3 | VA, Phase A, Minimum Average Demand Timestamp | TSTAMP
8493 | 3 | VA, Phase B, Minimum Average Demand Timestamp | TSTAMP
8496 | 3 | VA, Phase C, Minimum Average Demand Timestamp | TSTAMP
8499 | 3 | PF, (Q1+Q4), Phase A, Minimum Average Demand Timestamp | TSTAMP
8502 | 3 | PF, (Q1+Q4), Phase B, Minimum Average Demand Timestamp | TSTAMP
8505 | 3 | PF, (Q1+Q4), Phase C, Minimum Average Demand Timestamp | TSTAMP
8508 | 3 | PF, (Q2+Q3), Phase A, Minimum Average Demand Timestamp | TSTAMP
8511 | 3 | PF, (Q2+Q3), Phase B, Minimum Average Demand Timestamp | TSTAMP
8514 | 3 | PF, (Q2+Q3), Phase C, Minimum Average Demand Timestamp | TSTAMP
8517 | 3 | V A-N, %THD, Minimum Timestamp | TSTAMP
8520 | 3 | V B-N, %THD, Minimum Timestamp | TSTAMP
8523 | 3 | V C-N, %THD, Minimum Timestamp | TSTAMP
8526 | 3 | I A, %THD, Minimum Timestamp | TSTAMP
8529 | 3 | I B, %THD, Minimum Timestamp | TSTAMP
8532 | 3 | I C, %THD, Minimum Timestamp | TSTAMP
8535 | 3 | Symmetrical Comp Magnitude, 0 Seq, Minimum Timestamp | TSTAMP
8538 | 3 | Symmetrical Comp Magnitude, + Seq, Minimum Timestamp | TSTAMP
8541 | 3 | Symmetrical Comp Magnitude, - Seq, Minimum Timestamp | TSTAMP
8544 | 3 | Symmetrical Comp Phase, 0 Seq, Minimum Timestamp | TSTAMP
8547 | 3 | Symmetrical Comp Phase, + Seq, Minimum Timestamp | TSTAMP
8550 | 3 | Symmetrical Comp Phase, - Seq, Minimum Timestamp | TSTAMP
8553 | 3 | Unbalance, 0 Seq, Minimum Timestamp | TSTAMP
8556 | 3 | Unbalance, - Seq, Minimum Timestamp | TSTAMP
8559 | 3 | Current Unbalance, Minimum Timestamp | TSTAMP
8562 | 3 | W, (Q1), Total, Minimum Average Demand Timestamp | TSTAMP
8565 | 3 | VAR, (Q1), Total, Minimum Average Demand Timestamp | TSTAMP
8568 | 3 | VA, (Q1), Total, Minimum Average Demand Timestamp | TSTAMP
8571 | 3 | W, (Q1), Phase A, Minimum Average Demand Timestamp | TSTAMP
8574 | 3 | W, (Q1), Phase B, Minimum Average Demand Timestamp | TSTAMP
8577 | 3 | W, (Q1), Phase C, Minimum Average Demand Timestamp | TSTAMP
8580 | 3 | AR, (Q1), Phase A, Minimum Average Demand Timestamp | TSTAMP
8583 | 3 | VAR, (Q1), Phase B, Minimum Average Demand Timestamp | TSTAMP
8586 | 3 | VAR, (Q1), Phase C, Minimum Average Demand Timestamp | TSTAMP
8589 | 3 | VA, (Q1), Phase A, Minimum Average Demand Timestamp | TSTAMP
8592 | 3 | VA, (Q1), Phase B, Minimum Average Demand Timestamp | TSTAMP
8595 | 3 | VA, (Q1), Phase C, Minimum Average Demand Timestamp | TSTAMP
8598 | 3 | W, (Q2), Total, Minimum Average Demand Timestamp | TSTAMP
8601 | 3 | VAR, (Q2), Total, Minimum Average Demand Timestamp | TSTAMP
8604 | 3 | VA, (Q2), Total, Minimum Average Demand Timestamp | TSTAMP
8607 | 3 | W, (Q2), Phase A, Minimum Average Demand Timestamp | TSTAMP
8610 | 3 | W, (Q2), Phase B, Minimum Average Demand Timestamp | TSTAMP
8613 | 3 | W, (Q2), Phase C, Minimum Average Demand Timestamp | TSTAMP
8616 | 3 | VAR, (Q2), Phase A, Minimum Average Demand Timestamp | TSTAMP
8619 | 3 | VAR, (Q2), Phase B, Minimum Average Demand Timestamp | TSTAMP
8622 | 3 | VAR, (Q2), Phase C, Minimum Average Demand Timestamp | TSTAMP
8625 | 3 | VA, (Q2), Phase A, Minimum Average Demand Timestamp | TSTAMP
8628 | 3 | VA, (Q2), Phase B, Minimum Average Demand Timestamp | TSTAMP
8631 | 3 | VA, (Q2), Phase C, Minimum Average Demand Timestamp | TSTAMP
8634 | 3 | W, (Q3), Total, Minimum Average Demand Timestamp | TSTAMP
8637 | 3 | VAR, (Q3), Total, Minimum Average Demand Timestamp | TSTAMP
8640 | 3 | VA, (Q3), Total, Minimum Average Demand Timestamp | TSTAMP
8643 | 3 | W, (Q3), Phase A, Minimum Average Demand Timestamp | TSTAMP
8646 | 3 | W, (Q3), Phase B, Minimum Average Demand Timestamp | TSTAMP
8649 | 3 | W, (Q3), Phase C, Minimum Average Demand Timestamp | TSTAMP
8652 | 3 | VAR, (Q3), Phase A, Minimum Average Demand Timestamp | TSTAMP
8655 | 3 | VAR, (Q3), Phase B, Minimum Average Demand Timestamp | TSTAMP
8658 | 3 | VAR, (Q3), Phase C, Minimum Average Demand Timestamp | TSTAMP
8661 | 3 | VA, (Q3), Phase A, Minimum Average Demand Timestamp | TSTAMP
8664 | 3 | VA, (Q3), Phase B, Minimum Average Demand Timestamp | TSTAMP
8667 | 3 | VA, (Q3), Phase C, Minimum Average Demand Timestamp | TSTAMP
8670 | 3 | W, (Q4), Total, Minimum Average Demand Timestamp | TSTAMP
8673 | 3 | VAR, (Q4), Total, Minimum Average Demand Timestamp | TSTAMP
8676 | 3 | VA, (Q4), Total, Minimum Average Demand Timestamp | TSTAMP
8679 | 3 | W, (Q4), Phase A, Minimum Average Demand Timestamp | TSTAMP
8682 | 3 | W, (Q4), Phase B, Minimum Average Demand Timestamp | TSTAMP
8685 | 3 | W, (Q4), Phase C, Minimum Average Demand Timestamp | TSTAMP
8688 | 3 | VAR, (Q4), Phase A, Minimum Average Demand Timestamp | TSTAMP
8691 | 3 | VAR, (Q4), Phase B, Minimum Average Demand Timestamp | TSTAMP
8694 | 3 | VAR, (Q4), Phase C, Minimum Average Demand Timestamp | TSTAMP
8697 | 3 | VA, (Q4), Phase A, Minimum Average Demand Timestamp | TSTAMP
8700 | 3 | VA, (Q4), Phase B, Minimum Average Demand Timestamp | TSTAMP
8703 | 3 | VA, (Q4), Phase C, Minimum Average Demand Timestamp | TSTAMP
8706 | 3 | VA, (Q1+Q4), Total, Minimum Average Demand Timestamp | TSTAMP
8709 | 3 | VA, (Q1+Q4), Phase A, Minimum Average Demand Timestamp | TSTAMP
8712 | 3 | VA, (Q1+Q4), Phase B, Minimum Average Demand Timestamp | TSTAMP
8715 | 3 | VA, (Q1+Q4), Phase C, Minimum Average Demand Timestamp | TSTAMP
8718 | 3 | VA, (Q2+Q3), Total, Minimum Average Demand Timestamp | TSTAMP
8721 | 3 | VA, (Q2+Q3), Phase A, Minimum Average Demand Timestamp | TSTAMP
8724 | 3 | VA, (Q2+Q3), Phase B, Minimum Average Demand Timestamp | TSTAMP
8727 | 3 | VA, (Q2+Q3), Phase C, Minimum Average Demand Timestamp | TSTAMP
8730 | 3 | V A-N, Minimum Average Demand Timestamp | TSTAMP
8733 | 3 | V B-N, Minimum Average Demand Timestamp | TSTAMP
8736 | 3 | V C-N, Minimum Average Demand Timestamp | TSTAMP
8739 | 3 | V A-B, Minimum Average Demand Timestamp | TSTAMP
8742 | 3 | V B-C, Minimum Average Demand Timestamp | TSTAMP
8745 | 3 | V C-A, Minimum Average Demand Timestamp | TSTAMP
8748 | 3 | I A, %TDD, Minimum Timestamp | TSTAMP
8751 | 3 | I B, %TDD, Minimum Timestamp | TSTAMP
8754 | 3 | I C, %TDD, Minimum Timestamp | TSTAMP
8757 | 3 | I A, K-factor, Minimum Timestamp | TSTAMP
8760 | 3 | I B, K-factor, Minimum Timestamp | TSTAMP
8763 | 3 | I C, K-factor, Minimum Timestamp | TSTAMP
8766 | 3 | +Q,Total,Minimum Average Demand Timestamp | TSTAMP
8769 | 3 | +Q,Phase A, Minimum Average Demand Timestamp | TSTAMP
8772 | 3 | +Q,Phase Minimum Average Demand Timestamp | TSTAMP
8775 | 3 | +Q,Phase C, Minimum Average Demand Timestamp | TSTAMP
8778 | 3 | -Q,Total, Minimum Average Demand Timestamp | TSTAMP
8781 | 3 | -Q,Phase A, Minimum Average Demand Timestamp | TSTAMP
8784 | 3 | -Q,Phase Minimum Average Demand Timestamp | TSTAMP
8787 | 3 | -Q,Phase C, Minimum Average Demand Timestamp | TSTAMP
8790 | 3 | Aggregator 1,Minimum Average Demand Timestamp | FLOAT
8793 | 3 | Aggregator 2,Minimum Average Demand Timestamp | FLOAT
8796 | 3 | Aggregator 3,Minimum Average Demand Timestamp | FLOAT
8799 | 3 | Aggregator 4,Minimum Average Demand Timestamp | FLOAT
8802 | 3 | Option card 1 input accumulator 1,Minimum Average Demand Timestamp | FLOAT
8805 | 3 | Option card 1 input accumulator 2,Minimum Average Demand Timestamp | FLOAT
8808 | 3 | Option card 1 input accumulator 3,Minimum Average Demand Timestamp | FLOAT
8811 | 3 | Option card 1 input accumulator 4,Minimum Average Demand Timestamp | FLOAT
8814 | 3 | Option card 2 input accumulator 1,Minimum Average Demand Timestamp | FLOAT
8817 | 3 | Option card 2 input accumulator 2,Minimum Average Demand Timestamp | FLOAT
8820 | 3 | Option card 2 input accumulator 3,Minimum Average Demand Timestamp | FLOAT
8823 | 3 | Option card 2 input accumulator 4,Minimum Average Demand Timestamp | FLOAT
8976 | 2 | V A-N, previous Demand interval Short Term Maximum | FLOAT
8978 | 2 | V B-N, previous Demand interval Short Term Maximum | FLOAT
8980 | 2 | V C-N, previous Demand interval Short Term Maximum | FLOAT
8982 | 2 | V A-B, previous Demand interval Short Term Maximum | FLOAT
8984 | 2 | V B-C, previous Demand interval Short Term Maximum | FLOAT
8986 | 2 | V C-A, previous Demand interval Short Term Maximum | FLOAT
8988 | 2 | V A-N, Short Term Maximum | FLOAT
8990 | 2 | V B-N, Short Term Maximum | FLOAT
8992 | 2 | V C-N, Short Term Maximum | FLOAT
8994 | 2 | V A-B, Short Term Maximum | FLOAT
8996 | 2 | V B-C, Short Term Maximum | FLOAT
8998 | 2 | V C-A, Short Term Maximum | FLOAT
9000 | 2 | V A-N, Maximum | FLOAT
9002 | 2 | V B-N, Maximum | FLOAT
9004 | 2 | V C-N, Maximum | FLOAT
9006 | 2 | V A-B, Maximum | FLOAT
9008 | 2 | V B-C, Maximum | FLOAT
9010 | 2 | V C-A, Maximum | FLOAT
9012 | 2 | I A, Maximum Average Demand | FLOAT
9014 | 2 | I B, Maximum Average Demand | FLOAT
9016 | 2 | I C, Maximum Average Demand | FLOAT
9018 | 2 | W, (Q1+Q4), Total, Maximum Average Demand | FLOAT
9020 | 2 | VAR, (Q1+Q2), Total, Maximum Average Demand | FLOAT
9022 | 2 | W, (Q2+Q3), Total, Maximum Average Demand | FLOAT
9024 | 2 | VAR, (Q3+Q4), Total, Maximum Average Demand | FLOAT
9026 | 2 | VA, Total, Maximum Average Demand | FLOAT
9028 | 2 | PF, (Q1+Q4), Total, Maximum Average Demand | FLOAT
9030 | 2 | PF, (Q2+Q3), Total, Maximum Average Demand | FLOAT
9032 | 2 | Frequency, Maximum | FLOAT
9034 | 2 | Neutral Current, Maximum Average Demand | FLOAT
9036 | 2 | W, (Q1+Q4), Phase A, Maximum Average Demand | FLOAT
9038 | 2 | W, (Q1+Q4), Phase B, Maximum Average Demand | FLOAT
9040 | 2 | W, (Q1+Q4), Phase C, Maximum Average Demand | FLOAT
9042 | 2 | VAR, (Q1+Q2), Phase A, Maximum Average Demand | FLOAT
9044 | 2 | VAR, (Q1+Q2), Phase B, Maximum Average Demand | FLOAT
9046 | 2 | VAR, (Q1+Q2), Phase C, Maximum Average Demand | FLOAT
9048 | 2 | W, (Q2+Q3), Phase A, Maximum Average Demand | FLOAT
9050 | 2 | W, (Q2+Q3), Phase B, Maximum Average Demand | FLOAT
9052 | 2 | W, (Q2+Q3), Phase C, Maximum Average Demand | FLOAT
9054 | 2 | VAR, (Q3+Q4), Phase A, Maximum Average Demand | FLOAT
9056 | 2 | VAR, (Q3+Q4), Phase B, Maximum Average Demand | FLOAT
9058 | 2 | VAR, (Q3+Q4), Phase C, Maximum Average Demand | FLOAT
9060 | 2 | VA, Phase A, Maximum Average Demand | FLOAT
9062 | 2 | VA, Phase B, Maximum Average Demand | FLOAT
9064 | 2 | VA, Phase C, Maximum Average Demand | FLOAT
9066 | 2 | PF, (Q1+Q4), Phase A, Maximum Average Demand | FLOAT
9068 | 2 | PF, (Q1+Q4), Phase B, Maximum Average Demand | FLOAT
9070 | 2 | PF, (Q1+Q4), Phase C, Maximum Average Demand | FLOAT
9072 | 2 | PF, (Q2+Q3), Phase A, Maximum Average Demand | FLOAT
9074 | 2 | PF, (Q2+Q3), Phase B, Maximum Average Demand | FLOAT
9076 | 2 | PF, (Q2+Q3), Phase C, Maximum Average Demand | FLOAT
9078 | 1 | V A-N, %THD, Maximum | UINT16
9079 | 1 | V B-N, %THD, Maximum | UINT16
9080 | 1 | V C-N, %THD, Maximum | UINT16
9081 | 1 | I A, %THD, Maximum | UINT16
9082 | 1 | I B, %THD, Maximum | UINT16
9083 | 1 | I C, %THD, Maximum | UINT16
9084 | 2 | Symmetrical Component Magnitude, 0 Seq, Maximum | FLOAT
9086 | 2 | Symmetrical Component Magnitude, + Seq, Maximum | FLOAT
9088 | 2 | Symmetrical Component Magnitude, - Seq, Maximum | FLOAT
9090 | 1 | Symmetrical Component Phase, 0 Seq, Maximum | SINT16
9091 | 1 | Symmetrical Component Phase, + Seq, Maximum | SINT16
9092 | 1 | Symmetrical Component Phase, - Seq, Maximum | SINT16
9093 | 1 | Unbalance, 0 Seq, Maximum | UINT16
9094 | 1 | Unbalance, - Seq, Maximum | UINT16
9095 | 1 | Current Unbalance, Maximum | UINT16
9096 | 2 | W, (Q1), Total, Maximum Average Demand | FLOAT
9098 | 2 | VAR, (Q1), Total, Maximum Average Demand | FLOAT
9100 | 2 | VA, (Q1), Total, Maximum Average Demand | FLOAT
9102 | 2 | W, (Q1), Phase A, Maximum Average Demand | FLOAT
9104 | 2 | W, (Q1), Phase B, Maximum Average Demand | FLOAT
9106 | 2 | W, (Q1), Phase C, Maximum Average Demand | FLOAT
9108 | 2 | VAR, (Q1), Phase A, Maximum Average Demand | FLOAT
9110 | 2 | VAR, (Q1), Phase B, Maximum Average Demand | FLOAT
9112 | 2 | VAR, (Q1), Phase C, Maximum Average Demand | FLOAT
9114 | 2 | VA, (Q1), Phase A, Maximum Average Demand | FLOAT
9116 | 2 | VA, (Q1), Phase B, Maximum Average Demand | FLOAT
9118 | 2 | VA, (Q1), Phase C, Maximum Average Demand | FLOAT
9120 | 2 | W, (Q2), Total, Maximum Average Demand | FLOAT
9122 | 2 | VAR, (Q2), Total, Maximum Average Demand | FLOAT
9124 | 2 | VA, (Q2), Total, Maximum Average Demand | FLOAT
9126 | 2 | W, (Q2), Phase A, Maximum Average Demand | FLOAT
9128 | 2 | W, (Q2), Phase B, Maximum Average Demand | FLOAT
9130 | 2 | W, (Q2), Phase C, Maximum Average Demand | FLOAT
9132 | 2 | VAR, (Q2), Phase A, Maximum Average Demand | FLOAT
9134 | 2 | VAR, (Q2), Phase B, Maximum Average Demand | FLOAT
9136 | 2 | VAR, (Q2), Phase C, Maximum Average Demand | FLOAT
9138 | 2 | VA, (Q2), Phase A, Maximum Average Demand | FLOAT
9140 | 2 | VA, (Q2), Phase B, Maximum Average Demand | FLOAT
9142 | 2 | VA, (Q2), Phase C, Maximum Average Demand | FLOAT
9144 | 2 | W, (Q3), Total, Maximum Average Demand | FLOAT
9146 | 2 | VAR, (Q3), Total, Maximum Average Demand | FLOAT
9148 | 2 | VA, (Q3), Total, Maximum Average Demand | FLOAT
9150 | 2 | W, (Q3), Phase A, Maximum Average Demand | FLOAT
9152 | 2 | W, (Q3), Phase B, Maximum Average Demand | FLOAT
9154 | 2 | W, (Q3), Phase C, Maximum Average Demand | FLOAT
9156 | 2 | VAR, (Q3), Phase A, Maximum Average Demand | FLOAT
9158 | 2 | VAR, (Q3), Phase B, Maximum Average Demand | FLOAT
9160 | 2 | VAR, (Q3), Phase C, Maximum Average Demand | FLOAT
9162 | 2 | VA, (Q3), Phase A, Maximum Average Demand | FLOAT
9164 | 2 | VA, (Q3), Phase B, Maximum Average Demand | FLOAT
9166 | 2 | VA, (Q3), Phase C, Maximum Average Demand | FLOAT
9168 | 2 | W, (Q4), Total, Maximum Average Demand | FLOAT
9170 | 2 | VAR, (Q4), Total, Maximum Average Demand | FLOAT
9172 | 2 | VA, (Q4), Total, Maximum Average Demand | FLOAT
9174 | 2 | W, (Q4), Phase A, Maximum Average Demand | FLOAT
9176 | 2 | W, (Q4), Phase B, Maximum Average Demand | FLOAT
9178 | 2 | W, (Q4), Phase C, Maximum Average Demand | FLOAT
9180 | 2 | VAR, (Q4), Phase A, Maximum Average Demand | FLOAT
9182 | 2 | VAR, (Q4), Phase B, Maximum Average Demand | FLOAT
9184 | 2 | VAR, (Q4), Phase C, Maximum Average Demand | FLOAT
9186 | 2 | VA, (Q4), Phase A, Maximum Average Demand | FLOAT
9188 | 2 | VA, (Q4), Phase B, Maximum Average Demand | FLOAT
9190 | 2 | VA, (Q4), Phase C, Maximum Average Demand | FLOAT
9192 | 2 | VA (Q1+Q4),Total,Maximum Average Demand | FLOAT
9194 | 2 | VA (Q1+Q4),Phase A,Maximum Average Demand | FLOAT
9196 | 2 | VA (Q1+Q4),Phase B,Maximum Average Demand | FLOAT
9198 | 2 | VA (Q1+Q4),Phase C,Maximum Average Demand | FLOAT
9200 | 2 | VA (Q2+Q3),Total,Maximum Average Demand | FLOAT
9202 | 2 | VA (Q2+Q3),Phase A,Maximum Average Demand | FLOAT
9204 | 2 | VA (Q2+Q3),Phase B,Maximum Average Demand | FLOAT
9206 | 2 | VA (Q2+Q3),Phase C,Maximum Average Demand | FLOAT
9208 | 2 | V A-N, Average, Maximum Average Demand | FLOAT
9210 | 2 | V B-N, Maximum Average Demand | FLOAT
9212 | 2 | V C-N, Maximum Average Demand | FLOAT
9214 | 2 | V A-B, Maximum Average Demand | FLOAT
9216 | 2 | V B-C, Maximum Average Demand | FLOAT
9218 | 2 | V C-A, Maximum Average Demand | FLOAT
9220 | 1 | I A, %TDD, Maximum | UINT16
9221 | 1 | I B, %TDD, Maximum | UINT16
9222 | 1 | I C, %TDD, Maximum | UINT16
9223 | 1 | I A, K-factor, Maximum | UINT16
9224 | 1 | I B, K-factor, Maximum | UINT16
9225 | 1 | I C, K-factor, Maximum | UINT16
9226 | 2 | +Q,Total,Maximum Average Demand | FLOAT
9228 | 2 | +Q,Phase A,Maximum Average Demand | FLOAT
9230 | 2 | +Q,Phase B,Maximum Average Demand | FLOAT
9232 | 2 | +Q,Phase C, Maximum Average Demand | FLOAT
9234 | 2 | -Q,Total,Maximum Average Demand | FLOAT
9236 | 2 | -Q,Phase A,Maximum Average Demand | FLOAT
9238 | 2 | -Q,Phase B,Maximum Average Demand | FLOAT
9240 | 2 | -Q,Phase C, Maximum Average Demand | FLOAT
9242 | 2 | Aggregator 1, Maximum Average Demand | FLOAT
9244 | 2 | Aggregator 2, Maximum Average Demand | FLOAT
9246 | 2 | Aggregator 3, Maximum Average Demand | FLOAT
9248 | 2 | Aggregator 4, Maximum Average Demand | FLOAT
9250 | 2 | Option card 1 input accumulator 1, Maximum Average Demand | FLOAT
9252 | 2 | Option card 1 input accumulator 2, Maximum Average Demand | FLOAT
9254 | 2 | Option card 1 input accumulator 3, Maximum Average Demand | FLOAT
9256 | 2 | Option card 1 input accumulator 4, Maximum Average Demand | FLOAT
9258 | 2 | Option card 2 input accumulator 1, Maximum Average Demand | FLOAT
9260 | 2 | Option card 2 input accumulator 2, Maximum Average Demand | FLOAT
9262 | 2 | Option card 2 input accumulator 3, Maximum Average Demand | FLOAT
9264 | 2 | Option card 2 input accumulator 4, Maximum Average Demand | FLOAT
9400 | 3 | V A-N, Maximum Timestamp | TSTAMP
9403 | 3 | V B-N, Maximum Timestamp | TSTAMP
9406 | 3 | V C-N, Maximum Timestamp | TSTAMP
9409 | 3 | V A-B, Maximum Timestamp | TSTAMP
9412 | 3 | V B-C, Maximum Timestamp | TSTAMP
9415 | 3 | V C-A, Maximum Timestamp | TSTAMP
9418 | 3 | I A, Maximum Average Demand Timestamp | TSTAMP
9421 | 3 | I B, Maximum Average Demand Timestamp | TSTAMP
9424 | 3 | I C, Maximum Average Demand Timestamp | TSTAMP
9427 | 3 | W, (Q1+Q4), Total, Maximum Average Demand Timestamp | TSTAMP
9430 | 3 | VAR, (Q1+Q2), Total, Maximum Average Demand Timestamp | TSTAMP
9433 | 3 | W, (Q2+Q3), Total, Maximum Average Demand Timestamp | TSTAMP
9436 | 3 | VAR, (Q3+Q4), Total, Maximum Average Demand Timestamp | TSTAMP
9439 | 3 | VA, Total, Maximum Average Demand Timestamp | TSTAMP
9442 | 3 | PF, (Q1+Q4), Total, Maximum Average Demand Timestamp | TSTAMP
9445 | 3 | PF, (Q2+Q3), Total, Maximum Average Demand Timestamp | TSTAMP
9448 | 3 | Frequency, Maximum Timestamp | TSTAMP
9451 | 3 | Neutral Current, Maximum Average Demand Timestamp | TSTAMP
9454 | 3 | W, (Q1+Q4), Phase A, Maximum Average Demand Timestamp | TSTAMP
9457 | 3 | W, (Q1+Q4), Phase B, Maximum Average Demand Timestamp | TSTAMP
9460 | 3 | W, (Q1+Q4), Phase C, Maximum Average Demand Timestamp | TSTAMP
9463 | 3 | VAR, (Q1+Q2), Phase A, Maximum Average Demand Timestamp | TSTAMP
9466 | 3 | VAR, (Q1+Q2), Phase B, Maximum Average Demand Timestamp | TSTAMP
9469 | 3 | VAR, (Q1+Q2), Phase C, Maximum Average Demand Timestamp | TSTAMP
9472 | 3 | W, (Q2+Q3), Phase A, Maximum Average Demand Timestamp | TSTAMP
9475 | 3 | W, (Q2+Q3), Phase B, Maximum Average Demand Timestamp | TSTAMP
9478 | 3 | W, (Q2+Q3), Phase C, Maximum Average Demand Timestamp | TSTAMP
9481 | 3 | VAR, (Q3+Q4), Phase A, Maximum Average Demand Timestamp | TSTAMP
9484 | 3 | VAR, (Q3+Q4), Phase B, Maximum Average Demand Timestamp | TSTAMP
9487 | 3 | VAR, (Q3+Q4), Phase C, Maximum Average Demand Timestamp | TSTAMP
9490 | 3 | VA, Phase A, Maximum Average Demand Timestamp | TSTAMP
9493 | 3 | VA, Phase B, Maximum Average Demand Timestamp | TSTAMP
9496 | 3 | VA, Phase C, Maximum Average Demand Timestamp | TSTAMP
9499 | 3 | PF, (Q1+Q4), Phase A, Maximum Average Demand Timestamp | TSTAMP
9502 | 3 | PF, (Q1+Q4), Phase B, Maximum Average Demand Timestamp | TSTAMP
9505 | 3 | PF, (Q1+Q4), Phase C, Maximum Average Demand Timestamp | TSTAMP
9508 | 3 | PF, (Q2+Q3), Phase A, Maximum Average Demand Timestamp | TSTAMP
9511 | 3 | PF, (Q2+Q3), Phase B, Maximum Average Demand Timestamp | TSTAMP
9514 | 3 | PF, (Q2+Q3), Phase C, Maximum Average Demand Timestamp | TSTAMP
9517 | 3 | V A-N, %THD, Maximum Timestamp | TSTAMP
9520 | 3 | V B-N, %THD, Maximum Timestamp | TSTAMP
9523 | 3 | V C-N, %THD, Maximum Timestamp | TSTAMP
9526 | 3 | I A, %THD, Maximum Timestamp | TSTAMP
9529 | 3 | I B, %THD, Maximum Timestamp | TSTAMP
9532 | 3 | I C, %THD, Maximum Timestamp | TSTAMP
9535 | 3 | Symmetrical Comp Magnitude, 0 Seq, Maximum Timestamp | TSTAMP
9538 | 3 | Symmetrical Comp Magnitude, + Seq, Maximum Timestamp | TSTAMP
9541 | 3 | Symmetrical Comp Magnitude, - Seq, Maximum Timestamp | TSTAMP
9544 | 3 | Symmetrical Comp Phase, 0 Seq, Maximum Timestamp | TSTAMP
9547 | 3 | Symmetrical Comp Phase, + Seq, Maximum Timestamp | TSTAMP
9550 | 3 | Symmetrical Comp Phase, - Seq, Maximum Timestamp | TSTAMP
9553 | 3 | Unbalance, 0 Seq, Maximum Timestamp | TSTAMP
9556 | 3 | Unbalance, - Seq, Maximum Timestamp | TSTAMP
9559 | 3 | Current Unbalance, Maximum Timestamp | TSTAMP
9562 | 3 | W, (Q1), Total, Maximum Average Demand Timestamp | TSTAMP
9565 | 3 | VAR, (Q1), Total, Maximum Average Demand Timestamp | TSTAMP
9568 | 3 | VA, (Q1), Total, Maximum Average Demand Timestamp | TSTAMP
9571 | 3 | W, (Q1), Phase A, Maximum Average Demand Timestamp | TSTAMP
9574 | 3 | W, (Q1), Phase B, Maximum Average Demand Timestamp | TSTAMP
9577 | 3 | W, (Q1), Phase C, Maximum Average Demand Timestamp | TSTAMP
9580 | 3 | VAR, (Q1), Phase A, Maximum Average Demand Timestamp | TSTAMP
9583 | 3 | VAR, (Q1), Phase B, Maximum Average Demand Timestamp | TSTAMP
9586 | 3 | VAR, (Q1), Phase C, Maximum Average Demand Timestamp | TSTAMP
9589 | 3 | VA, (Q1), Phase A, Maximum Average Demand Timestamp | TSTAMP
9592 | 3 | VA, (Q1), Phase B, Maximum Average Demand Timestamp | TSTAMP
9595 | 3 | VA, (Q1), Phase C, Maximum Average Demand Timestamp | TSTAMP
9598 | 3 | W, (Q2), Total, Maximum Average Demand Timestamp | TSTAMP
9601 | 3 | VAR, (Q2), Total, Maximum Average Demand Timestamp | TSTAMP
9604 | 3 | VA, (Q2), Total, Maximum Average Demand Timestamp | TSTAMP
9607 | 3 | W, (Q2), Phase A, Maximum Average Demand Timestamp | TSTAMP
9610 | 3 | W, (Q2), Phase B, Maximum Average Demand Timestamp | TSTAMP
9613 | 3 | W, (Q2), Phase C, Maximum Average Demand Timestamp | TSTAMP
9616 | 3 | VAR, (Q2), Phase A, Maximum Average Demand Timestamp | TSTAMP
9619 | 3 | VAR, (Q2), Phase B, Maximum Average Demand Timestamp | TSTAMP
9622 | 3 | VAR, (Q2), Phase C, Maximum Average Demand Timestamp | TSTAMP
9625 | 3 | VA, (Q2), Phase A, Maximum Average Demand Timestamp | TSTAMP
9628 | 3 | VA, (Q2), Phase B, Maximum Average Demand Timestamp | TSTAMP
9631 | 3 | VA, (Q2), Phase C, Maximum Average Demand Timestamp | TSTAMP
9634 | 3 | W, (Q3), Total, Maximum Average Demand Timestamp | TSTAMP
9637 | 3 | VAR, (Q3), Total, Maximum Average Demand Timestamp | TSTAMP
9640 | 3 | VA, (Q3), Total, Maximum Average Demand Timestamp | TSTAMP
9643 | 3 | W, (Q3), Phase A, Maximum Average Demand Timestamp | TSTAMP
9646 | 3 | W, (Q3), Phase B, Maximum Average Demand Timestamp | TSTAMP
9649 | 3 | W, (Q3), Phase C, Maximum Average Demand Timestamp | TSTAMP
9652 | 3 | VAR, (Q3), Phase A, Maximum Average Demand Timestamp | TSTAMP
9655 | 3 | VAR, (Q3), Phase B, Maximum Average Demand Timestamp | TSTAMP
9658 | 3 | VAR, (Q3), Phase C, Maximum Average Demand Timestamp | TSTAMP
9661 | 3 | VA, (Q3), Phase A, Maximum Average Demand Timestamp | TSTAMP
9664 | 3 | VA, (Q3), Phase B, Maximum Average Demand Timestamp | TSTAMP
9667 | 3 | VA, (Q3), Phase C, Maximum Average Demand Timestamp | TSTAMP
9670 | 3 | W, (Q4), Total, Maximum Average Demand Timestamp | TSTAMP
9673 | 3 | VAR, (Q4), Total, Maximum Average Demand Timestamp | TSTAMP
9676 | 3 | VA, (Q4), Total, Maximum Average Demand Timestamp | TSTAMP
9679 | 3 | W, (Q4), Phase A, Maximum Average Demand Timestamp | TSTAMP
9682 | 3 | W, (Q4), Phase B, Maximum Average Demand Timestamp | TSTAMP
9685 | 3 | W, (Q4), Phase C, Maximum Average Demand Timestamp | TSTAMP
9688 | 3 | VAR, (Q4), Phase A, Maximum Average Demand Timestamp | TSTAMP
9691 | 3 | VAR, (Q4), Phase B, Maximum Average Demand Timestamp | TSTAMP
9694 | 3 | VAR, (Q4), Phase C, Maximum Average Demand Timestamp | TSTAMP
9697 | 3 | VA, (Q4), Phase A, Maximum Average Demand Timestamp | TSTAMP
9700 | 3 | VA, (Q4), Phase B, Maximum Average Demand Timestamp | TSTAMP
9703 | 3 | VA, (Q4), Phase C, Maximum Average Demand Timestamp | TSTAMP
9706 | 3 | VA, (Q1+Q4), Total, Maximum Average Demand Timestamp | TSTAMP
9709 | 3 | VA, (Q1+Q4), Phase A, Maximum Average Demand Timestamp | TSTAMP
9712 | 3 | VA, (Q1+Q4), Phase B, Maximum Timestamp | TSTAMP
9715 | 3 | VA, (Q1+Q4), Phase C, Maximum Average Demand Timestamp | TSTAMP
9718 | 3 | VA, (Q2+Q3), Total, Maximum Average Demand Timestamp | TSTAMP
9721 | 3 | VA, (Q2+Q3), Phase A, Maximum Average Demand Timestamp | TSTAMP
9724 | 3 | VA, (Q2+Q3), Phase B, Maximum Average Demand Timestamp | TSTAMP
9727 | 3 | VA, (Q2+Q3), Phase C, Maximum Average Demand Timestamp | TSTAMP
9730 | 3 | V A-N, Maximum Average Demand Timestamp | TSTAMP
9733 | 3 | V B-N, Maximum Average Demand Timestamp | TSTAMP
9736 | 3 | V C-N, Maximum Average Demand Timestamp | TSTAMP
9739 | 3 | V A-B, Maximum Average Demand Timestamp | TSTAMP
9742 | 3 | V B-C, Maximum Average Demand Timestamp | TSTAMP
9745 | 3 | V C-A, Maximum Average Demand Timestamp | TSTAMP
9748 | 3 | I A, %TDD, Maximum Timestamp | TSTAMP
9751 | 3 | I B, %TDD, Maximum Timestamp | TSTAMP
9754 | 3 | I C, %TDD, Maximum Timestamp | TSTAMP
9757 | 3 | I A, K-factor, Maximum Timestamp | TSTAMP
9760 | 3 | I B, K-factor, Maximum Timestamp | TSTAMP
9763 | 3 | I C, K-factor, Maximum Timestamp | TSTAMP
9766 | 3 | +Q,Total,Maximum Average Demand Timestamp | TSTAMP
9769 | 3 | +Q,Phase A,Maximum Average Demand Timestamp | TSTAMP
9772 | 3 | +Q,Phase B,Maximum Average Demand Timestamp | TSTAMP
9775 | 3 | +Q,Phase C, Maximum Average Demand Timestamp | TSTAMP
9778 | 3 | -Q,Total,Maximum Average Demand Timestamp | TSTAMP
9781 | 3 | -Q,Phase A,Maximum Average Demand Timestamp | TSTAMP
9784 | 3 | -Q,Phase B,Maximum Average Demand Timestamp | TSTAMP
9787 | 3 | -Q,Phase C, Maximum Average Demand Timestamp | TSTAMP
9790 | 3 | Aggregator 1, Maximum Average Demand Timestamp | TSTAMP
9793 | 3 | Aggregator 2, Maximum Average Demand Timestamp | TSTAMP
9796 | 3 | Aggregator 3, Maximum Average Demand Timestamp | TSTAMP
9799 | 3 | Aggregator 4, Maximum Average Demand Timestamp | TSTAMP
9802 | 3 | Option card 1 input accumulator 1, Maximum Average Demand Timestamp | TSTAMP
9805 | 3 | Option card 1 input accumulator 2, Maximum Average Demand Timestamp | TSTAMP
9808 | 3 | Option card 1 input accumulator 3, Maximum Average Demand Timestamp | TSTAMP
9811 | 3 | Option card 1 input accumulator 4, Maximum Average Demand Timestamp | TSTAMP
9814 | 3 | Option card 2 input accumulator 1, Maximum Average Demand Timestamp | TSTAMP
9817 | 3 | Option card 2 input accumulator 2, Maximum Average Demand Timestamp | TSTAMP
9820 | 3 | Option card 2 input accumulator 3, Maximum Average Demand Timestamp | TSTAMP
9823 | 3 | Option card 2 input accumulator 4, Maximum Average Demand Timestamp | TSTAMP
9900 | 2 | I A, previous Demand interval Short Term Minimum | FLOAT
9902 | 2 | I B, previous Demand interval Short Term Minimum | FLOAT
9904 | 2 | I C, previous Demand interval Short Term Minimum | FLOAT
9906 | 2 | I N, previous Demand interval Short Term Minimum | FLOAT
9908 | 2 | I A, Short Term Minimum in Demand Interval | FLOAT
9910 | 2 | I B, Short Term Minimum in Demand Interval | FLOAT
9912 | 2 | I C, Short Term Minimum in Demand Interval | FLOAT
9914 | 2 | I N, Short Term Minimum in Demand Interval | FLOAT
9916 | 2 | I A, previous Demand interval Short Term Maximum | FLOAT
9918 | 2 | I B, previous Demand interval Short Term Maximum | FLOAT
9920 | 2 | I C, previous Demand interval Short Term Maximum | FLOAT
9922 | 2 | I N, previous Demand interval Short Term Maximum | FLOAT
9924 | 2 | I A, Short Term Maximum in Demand Interval | FLOAT
9926 | 2 | I B, Short Term Maximum in Demand Interval | FLOAT
9928 | 2 | I C, Short Term Maximum in Demand Interval | FLOAT
9930 | 2 | I N, Short Term Maximum in Demand Interval | FLOAT